## Sheet1
400 VAC / 220 VAC WITH AUXILIARY 24 VDC PB BATTERY AUXILIARY SYSTEM WITH DUAL ENCLOSED ALUMINUM HULL ELECTRODE EARTHING AND FLOATING IT GROUNDING FOR FLOATING STATION PUMP
SHORE POWER PLANT | P = 160 kW / EFFICIENCY = 160 / 0.95 = 165 kW FOR MAIN PUMP ELECTRICAL MOTOR
DECK WINCHES POSITIONING | P = 4 x 7.5 kW = 30 kW
AUTOMATION / PLC / HMI / 24 VDC BATTERY BUS | P = 3.0 kW
MAIN DECK / INTERNAL SAFETY LIGHTING | P = 1.5 kW
TOTAL ACTIVE POWER | P = 165 kW + 30 kW + 3.0 kW + 1.5 kW = 200 kW
STATION CAPACITY SIZING | APPARENT POWER = P / POWER FACTOR = 200 kW / 0.85 = 235 kVA
SAFETY MARGIN APPLIED | 235 kVA x 1.25 (SAFETY MARGIN FACTOR) = 294 kVA
STANDARD TRANSFORMER STATION / LAND SIDE TRANSFORMER | 315 kVA SHORE POWER TRANSFORMER STATION 400 V 3 PHASE 50 Hz
SHORE SIDE INFRASTRUCTURE SPECIFICATIONS | SHORE DISCONNECT TRANSFORMER - 1 x 315 kVA CAST-RESIN (DRY TYPE ) ISOLATION
DOCKSIDE SHORE CONNECTION BOX | 1 x IP66 - HEAVY DUTY STEEL OUTDOOR DISTRIBUTION ENCLOSURE
ONBOARD CIRCUIT BREAKER | 1 x 400 A, 3 POLE MCCB WITH ADJUSTABLE ELECTRONIC TRIP
TRAILING CABLE BUNDLE | FLEXIBLE HEAVY DUTY MARINE CABLE TYPE EPR / PCP RUBBER
WINCH TYPES | WINCH TYPES
4 x WINCHES | CONSTANT TENSION MOORING WINCHES - 4 x DISTRIBUTED IN 4 CORNERS OF THE PONTOON USING PROGRAMMABLE 7.5 KW VFD INDUCTION MOTORS
SIMPLIFIED POWER DISTRIBUTION TOPOLOGY | SIMPLIFIED POWER DISTRIBUTION TOPOLOGY
PRIMARY HIGH VOLTAGE MAIN POWER GRID AC | SHORE GRID SUPPLY 400V AC 3 PHASE 50 Hz, DELIVERED FROM THE 315 kVA DOCKSIDE ISOLATION TRANSFORMER VIA FLEXIBLE HEAVY DUTY TRAILING CABLE BUNDLE W1 INTO CB1
PRIMARY HIGH VOLTAGE MAIN POWER GRID AC | AUXILIARY GENERATOR POWER OUTPUT - 400V AC, 3 PHASE, 50 Hz, DELIVERED DIRECTLY FROM THE BRUSHLESS ALTERNATOR / GENERATOR OF THE 45 kW DIESEL GENERATOR INTO CB3
PRIMARY HIGH VOLTAGE MAIN POWER GRID AC | MAIN PUMP ELECTRIC MOTOR FEED 400 VAC, 3 PHASE, 50 Hz, CONTROLLED BY THE 160 kW VFD THROUGH CB4
COMPONENTS (COMPONENT TYPE) | COMPONENT TYPES / CATALOG INFORMATION
PROPULSION (A01) | MAIN ELECTRIC MOTOR - SIEMENS / 1LE1504 - CATALOG 3AB43 - 4AA4, SPECIFICATIONS 160 kW 3 PHASE ASYNCHRONOUS 400 V 50 Hz 4 POLE 1500 RPM, QUANTITY 1
PROPULSION (A02) | EMERGENCY BACKUP DIESEL ENGINE - CATALOG CUMMINS MARINE QSB6.7-M 245, SPECIFICATIONS 180 kW 1500 RPM CONTINUOUS MARINE PRIME INTERNAL COMBUSTION ENGINE, 4 STROKE DIESEL, QUANTITY 1
GENERATION (A03) | AUXILIARY DIESEL GENERATOR SET - CUMMINS ONAN MDDCE-45, SPECIFICATIONS 45 kW CONTIUOUS PRIME 400 VAC 3 PHASE 50 Hz, 1500 RPM
DISTRIBUTION (A04) | MAIN SWITCHBOARD (MSB)
DISTRIBUTION (A05) | ONBOARD MAIN BREAKER (CB1), CATALOG SCHNEIDER C40N3TM400 MT400, SPECIFICATIONS MCCB 3 POLE 400 A MICROLOGIC 5.2E ELECTRONIC TRIP, QUANTITY 1
DISTRIBUTION (A06) | BUS TIE BREAKER (CB2), CATALOG SCHNEIDER C16N3TM160 MOTOR, SPECIFICATIONS MCCB 3 POLE 160 A MICROLOGIC 2.2 ELECTRONIC TRIP, QUANTITY 1
DISTRIBUTION (A07) | AUXILIARY GENERATOR BREAKER (CB3), CATALOG SCHNEIDER C10N3TM100 MOTOR, SPECIFICATIONS MCCB 3 POLE 100 A THERMAL MAGNETIC TRIP, QUANTITY 1
DISTRIBUTION (A08) | PUMP MOTOR ISOLATION BREAKER (CB4), CATALOG SCHNEIDER C40N3TM320 MN, SPECIFICATIONS MCCB 3 POLE 320 A, MICROLOGIC 5.2E ELECTRONIC TRIP, QUANTITY 1
AUTOMATION (A09) | ATS POWER MANAGEMENT CONTROLLER, CATALOG DEIF DENMARK AGC-4 MKII, SPECIFICATIONS MARINE APPROVED POWER MANAGEMENT CONTROLLER, LINE SENSING, BOOLEAN LOGIC FOR CB BLOCKS, QUANTITY 1
AUTOMATION (A10) | CENTRAL PLC AUTOMATION PANEL, CATALOG S7 1500 CPU 1511-1 PN, QUANTITY 1
DECK GEAR (A11) | CONSTANT TENSION WINCHES, CATALOG MARKEY MACHINERY WES016 TYPE-CT, QUANTITY 1
DISTRIBUTION (A12) | DOCKSIDE SHORE TRANSFORMER STATION, CATALOG SCHNEIDER ELECTRICAL TRIHAL SERIES, SPECIFICATIONS 315 kVA CAST RESIN DRY TYPE TRANSFORMER, QUANTITY 1
DISTRIBUTION (A13) | ONBOARD UTILITIES TRANSFORMER, CATALOG SOLAHD HS19B10-MARINE, SPECIFICATIONS 10kVA MARINE DRY TYPE ISOLATION TRANSFORMER SINGLE PHASE 50 Hz 400 VAC / 220 VAC, QUANTITY 1
POWER ELECTRONICS (A14) | BATTERY CHARGER RECTIFIER, CATALOG MASTERVOLT MARINE MASS 23 100-3, SPECIFICATIONS 3 PHASE SMART POWER RECTIFIER 220 VAC / 24 V DC CONTINOUS RATED OUTPUT 100 A, QUANTITY 1
STORAGE (A15) | EMERGENCY BACKUP BATTERY BANK, CATALOG MASTERVOLT AGM 12V 100Ahn SPECIFICATIONS SEALED MAINTENANCE FREE MARINE ABSORBED GLASS MAT (AGM) LEAD ACID BATTERY CELLS 2 UNITS WIRED IN SERIES FOR 24 VDC / 100 Ah EMERGENCY SAFETY GRID, QUANTITY 1
EARTHING (A16) | HULL GROUNDING COPPER BUS SYSTEM, SPECIFICATIONS CUSTOM TINNED COPPER STRIP 50 x 5 MM TINNED COPPER GROUNDING BAR NETWORK MOUNTED ON STAND-OFF INSULATORS BOLTED DIRECTLY IN HULL STRUCTURE, QUANTITY 1
DISTRIBUTION (A17) | INSULATION MONITORING DEVICE (IMD), SPECIFICATIONS BENDER ISOMETER IR4-D4 SERIES FOR AC/DC SYSTEMS, QUANTITY 2
POWER ELECTRONICS (A18) | MAIN PUMP VFD UNIT, CATALOG SIEMENS 6SL3224-0BE31-5UA0, QUANTITY 1
POWER ELECTRONICS (A19) | MOORING WINCH 7.5 kW VFDs, CATALOG SIEMENS 6SL3210-1SE21-8UA0, QUANTITY 4
PROTECTION (A20) | CHECK AUTOCAD REPORT SHEET FOR FUSES
WIRING (CONSIDER TOTAL LENGTH WITH ADDITIONAL 10% ROUTING MULTIPLIER) (WIRE TYPE) | WIRING SIZING INFORMATION / ADDITIONAL INFORMATION
LAND SIDE TRANFORMER (DOCKSIDE 315 kVA XFMR) (W1) -> CONNECTION BOX -> PRIMARY MAIN SWITCHBOARD BUS ONBOARD INCOMER CB1 (W2) | 2 x 3 x 200 MM^2 (PHASES) / PHASE + 2 x 1 x 120 MM^2 (EARTH), DOCK -> CONNECTION BOX WIRING - MARINE M2XCH ARMORED COPPER QUANTITY 50, CONNECTION BOX -> ONBOARD MSB INCOMER CB1 WIRING - HEAVY TRAILING EPR SUBMERSIBLE QUANTITY 35
PRIMARY MAIN SWITCHBOARD FEEDER CB4 -> 160 kW ELECTRIC MOTOR (W3) | 3 x 150 MM^2 (PHASES) + 1 x 95 MM^2 (EARTH), MSB PUMP FEEDER (CB4) -> 160kW ELECTRIC MOTOR WIRING - MARINE M2XCH ARMORED COPPER, QUANTITY 30
45 kW GENERATOR SET -> SECONDARY SWITCHBOARD INCOMER CB3 (W4) | 3 x 35 MM^2 (PHASES) + 1 x 16 MM^2 (EARTH), 45kW GENERATOR / ALTERNATOR -> MSB GENERATOR INCOMER (CB3) WIRING - MARINE M2XCH ARMORED COPPERM , QUANTITY 15
SECONDARY SWITCHBOARD AUXILIARY BUS -> 4 x 7.5 kW MOORING WINCHES 1 2 3 4 (W5, W6, W7, W8) | 4 x 6 MM^2 (PHASES), MSB SECONDARY SWITCHBOARD AUXILIARY BUS -> PARALLEL WINCH 1 2 3 4 LOCAL DECK STARTER WIRING - MARINE M2XCH ARMORED COPPER, QUANTITY 35 EACH EXTRA FOR SPARES
SECONDARY SWITCHBOARD AUXILIARY BUS -> 10 kVA TRANSFORMER INPUT (W9) | 2 x 6 MM^2 (PHASES) + 1 x 6 MM^2 (EARTH) MSB SECONDARY SWITCHBOARD AUCILIARY BUS -> 10kVA UTILITIES XFMR INPUT WIRING - MARINE M2XCH ARMORED COPPER, QUANTITY 5
10 kVA TRANSFORMER OUTPUT -> 220 VAC DISTRIBUTION PANEL (W10) | 2 x 16 MM^2 (PHASES) + 1 X 16 MM^2 (EARTH) 10 kVA UTILITIES XFMR OUT -> 220 VAC DISTRIBUTION PANEL WIRING - MARINE M2XCH ARMORED COPPER, QUANTITY 5
220 VAC DISTTRIBUTION PANEL > MAIN DECK LED FLOODLIGHTS (W11) | 3 x 2.5 MM^2 (PHASES), WIRING - MARINE M2XCH ARMORED COPPER, QUANTITY 120
220 VAC DISTRIBUTION PANEL -> 100 A RECTIFIER CHARGER INPUT (W12) | 3 x 2.5 MM^2 (PHASES), WIRING - MARINE M2XCH ARMORED COPPER, QUANTITY 3
100 A RECTIFIER CHARGER OUTPUT -> 24 VDC BATTERY VAULT (W13) | 2 x 35 MM^2 (DC) + 1 x 16 MM^2 (EARTH), WIRING - MARINE FLEXIBLE M2XCH FLEXIBLE COPPER, QUANTITY 2
FUSED BATTERY BOX -> CENTRAL PLC ENCLOSED RAIL (W14) | 2 x 6 MM^2 (DC), WIRING - MARINE M2XCH ARMORED COPPER, QUANTITY 5
24 VDC BATTERY BUS -> NAVIGATION AND SIGNAL LIGHTS (W15) | 2 x 2.5 MM^2 (DC), WIRING - MARINE M2XCH ARMORED COPPER, QUANTITY 45
DEIF AGC - 4ATS PANEL (ATS CONTROLLER) -> PARALLEL MOTORIZED ONBOARD SHORE CB1 (W16), MOTORIZED BUS TIE CB2 (W17), MOTORIZED GEN BREAKER CB3 (W18), MOTORIZED MOTOR BREAKER CB4 (W19), 180kW DIESEL ICE STARTER ACTIVATED BY RELAY GROUP R5 (W20) | 12 x 1.5 MM^2, WIRING - MARINE M2XCH CONTROL, QUANTITY 10, 7 x 1.5 MM^2, WIRING - MARINE M2XCH CONTROL, QUANTITY 8, 12 x 1.5 MM^2, WIRING - MARINE M2XCH CONTROL, QUANTITY 5, 7 x 1.5 MM^2, WIRING - MARINE M2XCH CONTROL, QUANTITY 8, 4 x 1.5 MM^2, WIRING - MARINE M2XCH CONTROL, QUANTITY 15
BENDER IMD DEVICE 1 -> AUXILIARY SYSTEM BUSBAR (W21) | 3 x 1.5 MM^2 (PHASES), WIRING - MARINE 3 x 1.5 MM^2, QUANTITY 5
BENDER IMD DEVICE 2 -> MOTOR SIDE CB4 FEEDER (W22) | 3 x 1.5 MM^2 (PHASES), WIRING - MARINE 3 x 1.5 MM^2, QUANTITY 5
IMD MONITORING LOOP CONNECTIONS (W23) | 3 x 1.5 MM^2 (PHASES) MARINE CABLE STD / M2XCH, QUANTITY 10
FIELD SENSORS AND VALVES -> PLC AUTOMATION PANEL I/O (W24) | 4 x 2 x 0.75 MM^2 (AC / DC), WIRING - MARINE FM2XCH SHIELDED PAIRS, QUANTITY 200
SYSTEM INITIAL STATE DEFINITION | EXPLANATION
TO DEFINE THE INTIAL STATE A BUILT AUXILIARY CONTACT SWITCH IS USED. THE 160 kW VFD LEADING TO THE 160 kW ELECTRIC MOTOR HAS A SET OF AUXILIARY NO/NC CONTACTS CONNECTED TO THE ELECTIC MOTOR TOGGLE SWITCH (SW0) | IF SW0 IS TOGGLED ON THEN THE AUXILIARY CONTACT BECOMES CLOSED (LOGIC 1 FOR EMERGENCY OPERATION) IF SW0 IS TOGGLED OFF THEN THE AUXILIARY CONTACT BECOMES OPEN (LOGIC 0 FOR SHORE CHARGING OPERATION) -> PLC READS THIS AS A SIMPLE 24 VDC CONTROL SIGNAL PUMP_MOTOR_ON = TRUE -> WIRING FOR PLC AUTOMATION INPUT FROM THE CB4 BREAKER.
CONTROLS ALGORITHM | CB1, CB2, CB3, CB4 WITH CONTROL RELAYS
ATS CONTROLLER LOGIC PSEUDOCODE | FOR MAIN OPERATION - IF (CB1 = 0 (CLOSED) AND SW0 = 0 (LOGIC 0, OFF)) THEN CB2 = 0 (CLOSED), CB3 = 0 (OPEN), CB4 = 0 (CLOSED), R5 = 0 (OPEN) ELSE IF FOR EMERGENCY OPERATION IF (CB1 = 1 (OPEN) OR SW0 = 1 (LOGIC 1, ON)) THEN CB2 = 1 (OPEN), CB3 = 1 (CLOSED WITH DELAY AFTER CB4 ENERGIZES TO ENSURE THE 45kW GENERATOR/ALTERNATOR IS STABLE), CB4 = 1 (OPEN), R5 = 1 (CLOSED)
CONTROLS ALGORITHM EXPLANATION REGARDING FLOATING PUMP STATION CONFIGURATION
MAIN OPERATION
1) FOR MAIN OPERATION -> CB1 IS CLOSED -> 400 VAC PRIMARY MAIN BUS PASSES AND REACHES CB4 -> CB4 IS CLOSED -> GOES TO THE PUMP CONTROLS -> ACTIVATES THE ELECTRIC MOTOR -> ACTIVATES THE PUMP THROUGH DIRECT COUPLING
2) FOR MAIN OPERATION -> CB2 IS CLOSED -> 400 VAC PRIMARY MAIN BUS CONNECTS WITH THE 400 VAC SECONDARY AUXILIARY BUS -> PASSES THROUGH THE WINCH COLNTROLS -> 400 VAC SECONDARY AUXILIARY BUS POWERS THE FOUR WINCHES
2A) IN PARALLEL, 400 VAC SECONDARY AUXILIARY BUS CONNECTS THE THE 220 VAC DISTRIBUTION PANEL BUS AFTER THE UTILITY TRANSFORMER -> PASSES THROUGH THE LIGHTING CONTROLS -> POWER THE FLOOD LIGHTS
2B) IN PARALLEL, 220 VAC BUS PASSES THROUGH THE 220 VAC / 24 VDC RECTIFIER AND CHARGES THE 24 VDC BATTERY
3) BATTERY WILL CHARGE THE AUTOMATION / CONTROLS / PLC ELEMENTS IN THE CONTROL ROOM AND IT WILL CHARGE THE SIGNAL LIGHTS / LAMPS
4) CB3 AND R5 ARE OPEN, CB1 MUST BE CLOSED AND SW0 MUST BE OFF FOR THIS OPERATION TO BE SELECTED
EMERGENCY OPERATION
1) FOR EMERGENCY OPERATION -> R5 START SWITCH / RELAY IS CLOSED -> ICE MAIN GENERATOR IS ACTIVATED -> POWER THE PUMP MECHANICALLY THROUGH DIRECT COUPLING
2) FOR EMERGENY OPERATION -> CB3 MECHANICAL BREAKER IS CLOSED -> 400 VAC 45 kW AUXILIARY GENERATOR CONNECTS WITH 400 VAC SECONDARY AUXILIARY BUS -> PASSES THROUGH THE WINCH CONTROLS -> POWER THE FOUR WINCHES
2A) IN PARALLEL, 400 VAC SECONDARY AUXILIARY BUS WILL CONNECT TO THE 220 VAC DISTRIBUTION PANEL BUS AFTER THE UTILITY TRANSFORMER -> PASSES THROUGH THE LIGHTING CONTROLS -> POWER THE FLOOD LIGHTS
2B) IN PARALLEL, 220 VAC BUS PASSES THROUGH THE 220 VAC / 24 VDC RECTIFIER AND CHARGES THE 24 VDC BATTERY
3) BATTERY WILL CHARGE THE AUTOMATION / CONTROLS / PLC ELEMENTS IN THE CONTROL ROOM AND IT WILL CHARGE THE SIGNAL LIGHTS / LAMPS
4) CB2 AND CB2 ARE OPEN, EITHER CB1 MUST BE OPEN OR SW0 MUST BE ON -> ALL OTHER CASES NOT EVALUATING THE AND OPERATOR FOR THE MAIN OPERATION WILL AUTOMATICALLY TRIGGER THE EMERGENCY OPERATION -> THIS DEFINES THE INITIAL STATE DEFINITION
ADDITIONAL CONCEPT - VIRTUAL DISTRIBUTED ZIEGLER NICHOLS Kp Ki Kd CONTROLLER TO SYCHRONIZE / DISTRIBUTE THE RATE OF CHANGE AT WHICH DEVIATIONS OF POWER ARE SUPPLIED TO AC LIGHTING, WINCHES AND THE CENTRIFUGAL PUMP | dP/dt (TOTAL) = dP/dt (PUMP) + dP/dt (WINCHES) + dP/dt (AC LIGHTING) = 0 FROM THE GENERATOR'S SIDE WHILE SIMULTANEOUSLY REDUCING OSCILLATIONS, ADDITIONAL POWER CONSUMPTION, NUMBER OF COMPONENTS AND MINIMIZING LOSSES